Section 219.582  Bulk Gasoline Terminals

a)	No person shall cause or allow the transfer of gasoline into any delivery vessel from any bulk gasoline terminal unless:

1)	The bulk gasoline terminal is equipped with a vapor control system that limits emission of VOM to 80 mg/1 (0.00067 lbs/gal) of gasoline loaded;

2)	The vapor control system is operating and all vapors displaced in the loading of gasoline to the delivery vessel are vented only to the vapor control system;

3)	There is no liquid drainage from the loading device when it is not in use;

4)	All loading and vapor return lines are equipped with fittings which are vapor tight; and

5)	The delivery vessel displays the appropriate sticker pursuant to the requirements of Section 219.584(b) or (d) of this Part; or, if the terminal is driver-loaded, the terminal owner or operator shall be deemed to be in compliance with this Section when terminal access authorization is limited to those owners and/or operators of delivery vessels who have provided a current certification as required by Section 219.584(c)(3) of this Part.

b)	The operator of a bulk gasoline terminal shall:

1)	Operate the terminal vapor collection system and gasoline loading equipment in a manner that prevents:

A)	Gauge pressure from exceeding 18 inches of water and vacuum from exceeding 6 inches of water as measured as close as possible to the vapor hose connection; and

B)	A reading equal to or greater than 100 percent of the lower explosive limit (LEL measured as propane) when tested in accordance with the procedure described in EPA 450/2-78-051 Appendix B, incorporated by reference in Section 219.112 of this Part; and

C)	Avoidable leaks of liquid during loading or unloading operations.

2)	Provide a pressure tap or equivalent on the terminal vapor collection system in order to allow the determination of compliance with Section 219.582(d)(1)(A) of this Part; and

3)	Within 15 business days after discovery of the leak by the owner, operator, or the Agency repair and retest a vapor collection system which exceeds the limits of subsection (c)(1)(A) or (B) of this Section.

(Source:  Amended at 17 Ill. Reg. 16918, effective September 27, 1993)