Section 370.APPENDIX B   Table No. 2 – Commonly Used Quantities of Sewage Flows From Miscellaneous Type Facilities

| Type of Establishment |  | Gallons Per Person Per Day (Unless otherwise noted) |
| --- | --- | --- |
| Airports (per passenger) |  | 5 |
| Bathhouses and swimming pools |  | 10 |
| Camps: |  |  |
| Campground with central comfort stations |  | 35 |
| With flush toilets, no showers |  | 25 |
| Construction camps (semi-permanent) |  | 50 |
| Day camps (no meals served) |  | 15 |
| Resort camps (night and day) with limited plumbing |  | 50 |
| Luxury camps |  | 100 |
| Cottages and small dwellings with seasonal occupancy |  | 75 |
| Country clubs (per resident member) |  | 100 |
| Country clubs (per non-resident member present) |  | 25 |
| Dwellings: |  |  |
| Boarding houses |  | 50 |
| (additional for non-resident boarders) |  | 10 |
| Rooming houses |  | 40 |
| Factories (gallons per person, per shift, exclusive of industrial wastes) |  | 35 |
| Hospitals (per bed space) |  | 250 |
| Hotels with laundry (2 persons per room) per room |  | 150 |
| Institutions other than hospitals including Nursing Homes (per bed space) |  | 125 |
| Laundries-self service (gallons per wash) |  | 30 |
| Motels (per bed space) with laundry |  | 50 |
| Picnic parks (toilet wastes only per park user) |  | 5 |
| Picnic parks with bathouses, showers and flush toilets (per park user) |  | 10 |
| Restaurants (toilet and kitchen wastes per patron) |  | 10 |
| Restaurants (kitchen wastes per meal served) |  | 3 |
| Restaurants (additional for bars and cocktail lounges) |  | 2 |
| Schools: |  |  |
| Boarding |  | 100 |
| Day, without gyms, cafeterias or showers |  | 15 |
| Day, with gyms, cafeterias and showers |  | 25 |
| Day, with cafeterias, but without gyms or showers |  | 20 |
| Service stations (per vehicle served) |  | 5 |
| Swimming pools and bathouses |  | 10 |
| Theaters: |  |  |
| Movie (per auditorium seat) |  | 5 |
| Drive-in (per car space) |  | 10 |
| Travel trailer parks without individual water and sewer hook-ups (per space) |  | 50 |
| Travel trailer parks with individual water and sewer hook-ups (per space) |  | 100 |
| Workers: |  |  |
| Offices, schools and business establishments (per shift) |  | 15 |

(Source:  Amended at 21 Ill. Reg. 12444, effective August 28, 1997)