Section 602.250  Treatment Construction Applications

The following information must be submitted on plans for the construction of treatment facilities:

a)	all appurtenances, specific structures, or equipment having any connection with the planned water treatment improvements;

b)	detailed hydraulic profiles of water flowing through treatment systems;

c)	schematic plumbing for all structures and equipment;

d)	location of feeders, piping layout, and points of application;

e)	locations of the sources of pollution listed in 35 Ill. Adm. Code 604.150(a);

f)	for sites subject to flooding, the maximum flood level based upon the highest flood level specified in the best available information, such as the flood of record, the 100-year flood projection, or the 500-year flood projection;

g)	security provisions; and

h)	stability and corrosion control:

1)	existing and proposed finished water quality, including:

A)	Hardness;

B)	Calcium;

C)	Alkalinity;

D)	pH;

E)	Orthophosphate;

F)	Silicate;

G)	Total Dissolved Solids;

H)	Oxidation-reduction potential (ORP);

I)	Temperature;

J)	Chloride;

K)	Sulfate;

L)	Iron;

M)	Manganese;

N)	Chlorine residual (total);

O)	Chlorine residual (free); and

2)	a recommendation of the treatment necessary to reduce corrosion in household plumbing.

(Source:  Amended at 47 Ill. Reg. 7449, effective May 16, 2023)