Section 604.405  Forced or Induced Draft Aeration

Forced or induced draft aeration devices must be designed to:

a)	include a blower with a weatherproof motor in a tight housing and screened enclosure;

b)	insure adequate counter current of air through the enclosed aerator column;

c)	exhaust air directly to the outside atmosphere;

d)	include a down turned and 24 mesh screened air outlet and inlet;

e)	be such that air introduced in the column must be as free from obnoxious fumes, dust, and dirt as possible;

f)	be such that sections of the aerator can be reached or removed for maintenance of the interior or installed in a separate aerator room;

g)	provide loading at a rate of 1 to 5 gallons per minute for each square foot of total tray area (2.5 to 12.5 m/hr);

h)	ensure that the water outlet is sealed;

i)	discharge through a series of five or more trays with separation of trays not less than six inches;

j)	provide distribution of water uniformly over the top tray; and

k)	be of durable material resistant to the aggressiveness of the water and dissolved gases.