Section 604.1315  Vents

a)	Finished water storage structures must be vented as follows:

1)	the overflow pipe must not be considered a vent; and

2)	open construction between the sidewall and roof is not permissible.

b)	Vents must:

1)	prevent the entrance of surface water and rainwater;

2)	exclude birds and animals;

3)	exclude insects and dust to the extent practicable;

4)	on ground level structures, open downward with the opening at least 24 inches above the roof or sod and be covered with 24 mesh non-corrodible screen; and

5)	on elevated tanks and standpipes:

A)	open downward; and

B)	be fitted with either four mesh non-corrodible screen, or with finer mesh non-corrodible screen in combination with an automatically resetting pressure-vacuum relief mechanism, as required by the Agency.