Section 604.1450  Surface Water Crossings

a)	For above-water crossings, the pipe must be adequately supported and anchored, protected from damage and freezing, and accessible for repair or replacement.

b)	Underwater Crossings

1)	A minimum cover of five feet must be provided over the pipe.

2)	When crossing water courses that are greater than 15 feet in width, the following apply:

A)	the pipe must be of special construction, having flexible, restrained or welded watertight joints;

B)	valves must be provided at both ends of water crossings so that the section can be isolated for testing or repair;

C)	the valves must be easily accessible and not subject to flooding; and

D)	permanent taps or other provisions to allow insertion of a small meter to determine leakage and obtain water samples must be made on each side of the valve closest to the supply source.