**Section 160.40 Location of Tanks – Distance Between Aboveground Tanks**

a) The minimum distance from tanks to adjacent tanks shall be as follows:

|  |  |
| --- | --- |
| Tank Capacity(Gallons) | Minimum Distance(Feet) |
| 24,000 or less  | 5 |
| 24,001 to 48,000  | 10 |
| 48,001 to 75,000  | 13 |
| 75,001 to 100,000  | 15 |
| Over 100,000  | One Tank Diameter |

b) If tanks are of different capacities, the capacity of the larger tank shall govern its distance to adjacent tanks.

c) Existing tanks of under 24,000 gallons shall maintain a minimum distance of at least 3 feet.

(Source: Amended at 9 Ill. Reg. 10012, effective October 1, 1985)