Section 250.TABLE F   General Pressure Relationships and Ventilation of Certain Hospital Areas

| Area Designation | Pressure Relationship To Adjacent Areas | Minimum Total Air Changes Per Hour Supplied To Room | All Air Exhausted Directly To Outdoors | Recirculation Within Room Units |
| --- | --- | --- | --- | --- |
| Operating Room | + | 12 | Optional | No |
| Emergency Operating Room | + | 12 | Optional | No |
| Delivery Room | + | 12 | Optional | No |
| *Soiled Workroom or *Soiled Holding Room | - | 10 | Yes | No |
| *Clean Workroom or *Clean Holding Room | + | 4 | Optional | Optional |
| *Autopsy | - | 10 | Yes | No |
| *Toilet Room | - | 10 | Yes | No |
| *Bedpan Room | - | 10 | Yes | No |
| *Bathroom | - | 10 | Yes | No |
| *Janitors' Closet | - | 10 | Yes | No |
| *Sterilizer Equipment Room | - | 10 | Yes | No |
| *Food Preparation Centers | 0 | 10 | Yes | No |
| *Dietary Day Storage | 0 | 2 | Optional | No |
| *Laundry, General | 0 | 10 | Yes | No |
| *Soiled Linen Sorting and *Storage Rooms | - | 10 | Yes | No |
| *Anesthesia Storage | 0 | 8 | Yes | No |

Symbol Key:	+ = Positive	- = Negative	O= Equal * = Recommended

(Source:  Amended at 11 Ill. Reg. 10642, effective July 1, 1987)