Section 300.TABLE B   Pressure Relationships and Ventilation Rates of Certain Areas for New Intermediate Care Facilities and Skilled Nursing Facilities

| Area Designation |  |  | Pressure Relationship to Adjacent Areas | Minimum Air Changes Per Hour Supplied To Room | All Air Exhausted Directly Outdoors | Recirculated within Room Units |
| --- | --- | --- | --- | --- | --- | --- |
| Resident Rm |  |  | 0 | 2 | Optional | Optional |
| Medication Rm. |  |  | + | 4 | Optional | Optional |
| Clean Utility Rm. |  |  | + | 4 | Optional | Optional |
| Clean Linen Storage |  |  | + | 2 | Optional | Optional |
| Examination and Treatment Rm. |  |  | 0 | 2 | Optional | Optional |
| Physical Therapy |  |  | - | 4 | Optional | Optional |
| Occupational Therapy |  |  | - | 2 | Optional | Optional |
| Dietary Day Storage |  |  | 0 | 2 | Optional | No |
| Soiled Utility |  |  | - | 6 | Yes | No |
| Soiled Linen Holding Rm. |  |  | - | 6 | Yes | No |
| Soiled Linen & Trash Chute Rm. |  |  | - | 6 | Yes | No |
| Toilet Rm. |  |  | - | 6 | Yes | No |
| Shower Rm. |  |  | - | 6 | Yes | No |
| Bathroom |  |  | - | 6 | Yes | No |
| Janitors' Closet |  |  | - | 6 | Yes | No |
| Food Preparation Areas |  |  | 0 | 6 | Yes | No |
| Dishwashing |  |  | - | 6 | Yes | No |
| Laundry, General |  |  | 0 | 6 | Yes | No |
| Soiled Linen Sorting & Storage |  |  | - | 6 | Yes | No |
| + | = | Positive |  |  |  |  |
| - | = | Negative |  |  |  |  |
| 0 | = | Equal |  |  |  |  |
| The ventilation rates shown in the above TABLE shall be considered as minimum acceptable rates and shall not be construed as precluding the use of higher ventilation rates. |  |  |  |  |  |  |