Section 350.TABLE C   Construction Types and Sprinkler Requirements for Existing Intermediate Care Facilities for the Developmentally Disabled

| Construction Type |  |  |  | Stories |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | 1 | 2 | 3 | over 3 |
| 2-hour Fire Resistive |  |  |  | X | X |  | X |
| 1-hour Protected Noncombustible |  |  |  | X | X* | X* |  |
| Noncombustible |  |  |  | X* | X* | X* |  |
| Heavy Timber |  |  |  | X* | X* |  |  |
| 1-hour Protected Ordinary |  |  |  | X* | X* |  |  |
| 1-hour Protected Wood Frame |  |  |  | X* | X* |  |  |
| Ordinary |  |  |  | X* |  |  |  |
| Frame |  |  |  | X* |  |  |  |
| Key: | X | = | Allowed types of construction |  |  |  |  |
|  | * | = | Building requires automatic fire extinguishment protection |  |  |  |  |