Section 860.TABLE B   Water Distribution Pipe Size

| Inside Diameter of Main (In inches) | Number of Manufactured Home Sites Connected | Maximum Length of Main (In feet) |
| --- | --- | --- |
| 2 | 20 | 600 |
| 3 | 60 | 1,800 |
| 4 | 120 | 3,600 |
| 6 | 400 | 12,000 |

NOTE:	If local requirements exceed the above sizes, the local standards must be met.  A minimum 6-inch diameter pipe is required if fire hydrants are installed in the water distribution system.  (See Section 860.270(d).)

(Source:  Amended at 30 Ill. Reg. 13419, effective July 28, 2006)